## Slide 1: Constrained Deep Learning for Modeling and Control of Unknown Nonlinear Dynamical Systems
Jan Drgona
Collaborators: Elliott Skomski, Soumya Vasisht,
Aaron Tuor, Vikas Chandan, Draguna Vrabie
Talk at MERL, 29th of April 2021

## Slide 2: Model Predictive Control
95% of the process control applications are PID loops using trial and error rule-based optimization. The rest is model predictive control (MPC).
PID
Reactive
Simple
Field-level
Suboptimal
Unconstrained
Linear
SISO
MPC
Predictive
Complex
Supervisory-level
Optimal
Constrained
Nonlinear
MIMO
Assumption:
Reliable and accurate system dynamics model
Notes: Domain awareness, trusted autonomy
PID controller-
A PID controller continuously calculates an error value
the difference between a desired setpoint (SP) a process variable (PV) and
Correction based on proportion of error, integration of accumulated error, and derivative of the error
MPC first developed in the chemical industry to address some of the shortcomings of a PID controller.
Designed to handle MIMO systems
Can handle constraints
Preview capability
MPC uses a model to predict future outcomes of a process.
Online optimization problem at each process interval. Performs first action in the rollout.
requiring large memory and fast processor to operate in real time.
Training and calibration of models- lots of expert time
Optimization: translation to a solver language- lots of expert time
Computational limitations of control hardware depending on the system

## Slide 3: Implementation of MPC in Office Building in Belgium
The field test energy use performance of MPC (green) and RBC (red) during the transient season. Each dot represents one day.
The field test thermal comfort performance of MPC (green) and RBC (red) during the transient season. Each dot represents one day.
Highlights: Heat pump energy savings up to 53%.
Thermal comfort improvement up to 37%.
[1] Drgona J., et al., Cloud-based implementation of white-box model predictive control for a GEOTABS office building: a field test demonstration. Submitted to Journal of Process Control, 2019.
Notes: To better understand the complexity of the task, lets walk through a complete workflow as implemented for a practical use case to control an office building in Belgium.
This office building is equipped with thermally activated building structures with a geothermal heat pump (GEOTABS). These kinds of buildings are known to be very challenging to control due to the large thermal mass and associated time delays. For optimal operation of this type of systems, predictive control is an absolute must.
First one develops a high-fidelity physics-based model based on the available engineering documentation and measurement data.
Then the control-relevant equations are extracted and used to construct an optimization-based predictive controller.
The optimized controls are computed every 15min based on new weather forecast and new measurement from the building, then the controls are communicated to the building management system for execution.
The whole procedure takes approximately a minute to execute in real time.
After using the MPC in the office building for a couple of months the team measured more than 50% energy savings on the heat pump and improved thermal comfort by approximately 37%. The rigid and delayed behavior of the rule-based controller is replaced by dynamic and anticipatory behavior of MPC, which keeps the zone temperatures closer within comfort bounds and delivers cooling only when it is needed.

## Slide 4: MPC Challenges Limit its Broad Adoption
Modeling
  Physics-based modeling is expensive and time-consuming
  Purely data-driven models lack operational safety guarantees, and do not generalize well
Optimization: translation to a solver language
  Multiple customized methods for dealing with constraints (soft, hard)
  Multi-objective, convexification, regularization, convergence issues
Computational limitations of control hardware
  Online optimization computational requirements
  Cloud deployment vs embedded optimization
Acceptance by operators
  Installation: data mapping, sensor discovery, tuning
  Interpretability, interaction, trust
  Performance Measurement & Verification
Drgona J., J. Arroyo, I.C. Figueroa, D. Blum, K. Arendt, D. Kim, and E.P. Olle, J. Oravec, M.Wetter, D.L.Vrabie, L. Helsen. 2020. "All You Need to Know About Model Predictive Control for Buildings." Annual Reviews in Control, September 29, 2020
Notes: There are four main challenges that must be overcome to make MPC cost-effective
The Training and calibration of models – must be automated
The translation of the optimization problems to a solver language – must be automated
To address the computational limitations of embedded hardware - must reduce computing need without trading performance
Acceptance by building operators – complex decisions must be translated to interpretable decision rules

## Slide 5: Objective: Integrate Deep Learning with MPC and Physics
Automate learning of the system dynamics and model-based control policy
Streamline the installation process, facilitate explainability
Endow with lifelong learning and offer performance guarantees during the learning process

## Slide 6: Formulations of Constrained Optimization Problems
Standard form
Parametric programming
Lagrangian form
Machine learning
“online” optimization
Single solution for
given parameter values
“offline” optimization
Obtains a solution map
for a set of parameters
“offline” optimization
Obtains a model (map)
for a set of datapoints
“online” optimization
Using soft constraints
Instead of hard constraints
Notes: There are four main challenges that must be overcome to make MPC cost-effective
The Training and calibration of models – must be automated
The translation of the optimization problems to a solver language – must be automated
To address the computational limitations of embedded hardware - must reduce computing need without trading performance
Acceptance by building operators – complex decisions must be translated to interpretable decision rules

## Slide 7: Formulations of Constrained Optimization Problems
Standard form
Parametric programming
Lagrangian form
Machine learning
“online” optimization
Single solution for
given parameter values
“offline” optimization
Obtains a solution map
for a set of parameters
“offline” optimization
Obtains a model (map)
for a set of datapoints
“online” optimization
Using soft constraints
Instead of hard constraints
Data-driven differentiable parametric optimization: Combining principles of
Lagrangian formulation, parametric programming and ML
Notes: There are four main challenges that must be overcome to make MPC cost-effective
The Training and calibration of models – must be automated
The translation of the optimization problems to a solver language – must be automated
To address the computational limitations of embedded hardware - must reduce computing need without trading performance
Acceptance by building operators – complex decisions must be translated to interpretable decision rules

## Slide 8: Method: Differentiable Predictive Control (DPC)
Dataset of perturbed system measurements
Synthetic random dataset of references and system states
Stage I: System Identification
Stage II: Policy Optimization
Fixed SSM Parameters
System ID
Loss
Reference
Tracking
Loss
Notes: Integrate Deep Learning with Optimization-Based Control
Machine learning models that respect physical laws
Incorporate domain knowledge in their architectures
Incorporate domain knowledge with auxiliary loss functions
Use cases
Optimal control
Predictive maintenance
Surrogates for inverse problems
Forecasting for high level planning
Configurable optimization
Sequential
Joint
Alternating
Online updates
Scalable inference
Fast sampling rates
Limited computational resources
High dimensional state space
Long prediction horizons

## Slide 9: Constrained Neural State Space Models
Machine learning models that respect physical laws and constraints
Incorporate domain knowledge in their architectures
Incorporate domain knowledge with auxiliary loss functions
Block-structured neural state-space model
Neural state estimator
Learnable activation functions
Structured linear maps
Constraints enforcing penalties
  [1] Elliott Skomski, Soumya Vasisht, Colby Wight, Aaron Tuor, Jan Drgona, Draguna L Vrabie, Constrained Block Nonlinear Neural Dynamical Models, to appear in ACC 2021. arXiv:2101.01864, 2021
  [2] Aaron R Tuor, Ján Drgona, Draguna L Vrabie, Constrained neural ordinary differential equations with stability guarantees, ICLR Workshop on Integration of Deep Neural Models and Differential EquationsarXiv:2004.10883, 2020

## Slide 10: Neural Network Block Structure and Components
Multi-layer perceptron
  Function approximator
  Composed linear maps and nonlinear activation functions
  Model complicated functions
    adding depth (more layers)
    and/or width (more nodes)
Residual Neural Network
  Adds shortcut connections
  Easier to optimize
  Mitigates vanishing gradient
Recurrent Neural Network
  Adds recurrences from previous inputs
  Sequential modeling
  Can model time delay
f

## Slide 11: Structured Linear Maps with Eigenvalue Constraints
SVD factorization
Hamiltonian weight
  [1] Jiong Zhang, et al., Stabilizing Gradients for Deep Neural Networks via Efficient SVD Parameterization, 2018. Eldad Haber and Lars Ruthotto, Stable Architectures for Deep Neural Networks 2017 [2] Jan Drgona, Aaron Tuor, Soumya Vasisht, Elliott Skomski, Draguna Vrabie, Spectral Analysis and Stability of Deep Neural Dynamics, arXiv:2011.13492, 2020
Pytorch implementation: https://github.com/pnnl/slim

## Slide 12: Training Loss Includes System Knowledge
Bound influence of input and bound output to physical range
Predicted State Smoothing
Partially observable non-autonomous system
Data needs:
Optimize N-step prediction horizon MSE
Elliott Skomski, Jan Drgona, Aaron Tuor, Physics-Informed Neural State Space Models via Learning and Evolution, to appear in L4DC, 2021, arXiv:2011.13497

## Slide 13: Application: Real World Office Building

## Slide 14: Modeling Building Thermal Dynamics
Ján Drgona, Aaron R. Tuor, Vikas Chandan, Draguna L. Vrabie, Physics-constrained deep learning of multi-zone building thermal dynamics,
Energy and Buildings, 2021.

## Slide 15: Open-loop Trajectories of Linear Dynamics Model

## Slide 16: Open-loop Trajectories of Neural Dynamics Model

## Slide 17: System Identification Performance Comparison

## Slide 18: Deep Learning of Model-based Control Policies
Objectives
  Cut the development and deployment cost of model-based control
  Learn safe and robust control policies with adaptive updates
  Embedded hardware implementation
Approaches
  Approximate MPC
    Imitation learning of supervisory MPC
  Differentiable Predictive Control
    Supervised policy learning in closed loop guided by learned model and MPC loss

## Slide 19: Deep Learning-based Approximations of MPC
Drgona J., et al., “Approximate model predictive building control via machine learning,” Applied Energy, 2018
Drgona J., Helsen L., Vrabie D., “Stripping off the implementation complexity of physics-based model predictive control for buildings via deep learning.” NeurIPS Climate Change AI workshop, 2019.
Drgona J., Helsen L., Vrabie D.,"Cutting the Deployment Costs of Physics-Based MPC in Buildings by Simulation-Based Imitation Learning.”, proceedings of Dynamic Systems and Control Conference 2020, - Best paper award
  Cons
  Loosing performance guarantees
  Still relies on original MPC
  Pros
  Can accurately approximate MPC
  Low CPU and memory demands

## Slide 20: Differentiable Predictive Control (DPC)
Generic method for constrained model-based control
Can be trained end-to-end from time series dataset
Nonlinear constrained optimal control
Explicit neural network-based control policy
Scalability beyond the limitations of explicit MPC
[1] Jan Drgona, et al., Differentiable Predictive Control: An MPC Alternative for Unknown Nonlinear Systems using Constrained Deep Learning https://arxiv.org/abs/2011.03699
[2] Jan Drgona, Aaron Tuor, Draguna Vrabie, Constrained Physics-Informed Deep Learning for Stable System Identification and Control of Unknown Linear Systems https://arxiv.org/abs/2004.11184

## Slide 21: Capability: Computationally efficient performance optimization with operational safety constraints
Balancing conflicting objectives
Response to constraint tightening
Reference tracking performance
--- Reference trajectory
--- Constraints
__ Controlled trajectory
Notes: Computationally efficient performance optimization with operational safety constraints

## Slide 22: Model Predictive Control vs Differentiable Predictive Control
DPC = Formulation of MPC problem as a constrained deep learning model
  Drgona J., Tuor A., Vrabie D., Constrained Physics-Informed Deep Learning for Stable System Identification and Control of Linear Systems, Code release: https://github.com/pnnl/deps_arXiv2020

## Slide 23: Comparison of DPC with MPC, LQR, and RL
Closed loop trajectories. Top: controlled state (orange), internal model predictions (green), given reference (dashed blue), and constraints (dashed black). Middle: control action (blue) and bounds (dashed black). Bottom: disturbances
Control performance comparison in simulations with parametric and additive uncertainties. Control Strategies: MPC, Robust MPC , Stochastic MPC, LQR, LQI, A2C: Asynchronous, deterministic variant of Advantage Actor Critic, ACKTR: Actor Critic using Kronecker-Factored Trust Region, PPO2: Proximal Policy Optimization
  Drgona J., Tuor A., Vrabie D., Constrained Physics-Informed Deep Learning for Stable System Identification and Control of Linear Systems, Code release: https://github.com/pnnl/deps_arXiv2020

## Slide 24: DPC for Building Control
  Jan Drgona, Aaron Tuor, Elliott Skomski, Soumya Vasisht, Draguna Vrabie, Deep Learning Explicit Differentiable Predictive Control Laws for Buildings, accepted for IFAC NMPC 2021
model
policy
Economic MPC loss function

## Slide 25: Closed-loop Performance of DPC on Learned Model without Plant-Model Mismatch
  Jan Drgona, Aaron Tuor, Elliott Skomski, Soumya Vasisht, Draguna Vrabie, Deep Learning Explicit Differentiable Predictive Control Laws for Buildings, accepted for IFAC NMPC 2021

## Slide 26: Closed-loop Performance of DPC on Emulator Model with Plant-Model Mismatch
  Jan Drgona, Aaron Tuor, Elliott Skomski, Soumya Vasisht, Draguna Vrabie, Deep Learning Explicit Differentiable Predictive Control Laws for Buildings, accepted for IFAC NMPC 2021

## Slide 27: Embedded Implementation of DPC
Flexy-Air system sketch with Raspberry-Pi controller
Performance comparison: reference (red dashed), position controlled with PI controller (green), explicit model predictive control (purple), constrained differentiable predictive control (blue) and constraints (black-dashed). Bottom figures show the fan speed controls
  Jan Drgona, Karol Kis, Aaron Tuor, Draguna Vrabie, Martin Klauco, Differentiable Predictive Control: An MPC Alternative for Unknown Nonlinear Systems using Constrained Deep Learning; arXiv:2011.03699, under review

## Slide 28: Stability Analysis of Deep Neural Networks
Motivation
  Safety-critical and high-performance systems call for formal verification methods to ensure safe operation.
  Lack of guarantees on global and local behavior of DNNs still remain limiting factors.
  Properties like stability and robustness are crucial for reliable system identification and control.
Goal
  Apply system- and control-theoretic analysis methods on DNNs.
  Provide stability guarantees, identify regions of attraction and achieve desired dynamical behavior with DNNs.
  Jan Drgona, Aaron Tuor, Soumya Vasisht, Elliott Skomski, Draguna Vrabie, Spectral Analysis and Stability of Deep Neural Dynamics, arXiv:2011.13492

## Slide 29: Deep Neural Networks as Parameter Varying Affine Maps
At every point , the neural network, without bias may be represented as
where represent the weight parameterizations at layer , and is a diagonal matrix that represents the element-wise application of the nonlinear activation function at layer .
  Jan Drgona, Aaron Tuor, Soumya Vasisht, Elliott Skomski, Draguna Vrabie, Spectral Analysis and Stability of Deep Neural Dynamics, arXiv:2011.13492
Deep feedforward neural network
Notes: The presentation I’m giving today is for a data-driven method for dynamics modeling.
We should care about this because people interact with and depend on complicated systems all the time.
Greater understanding of these systems can lead to outcomes which are
More energy efficient
Cost effective
Conducive to human life
Having an accurate model of a system enables scientific discovery,
Can provide critical information to support high stakes decisions in changing environments
Or to provide necessary information for predictive maintenance of high value equipment, avoiding costly and potentially dangerous equipment
Failures.
One of the most common and lucrative uses of systems models are for predictive control in manufacturing and other large scale enterprises.
I’m presenting a method today which bridges benefits of traditional physics-based modeling with more recent data-driven modeling using deep learning
Traditional physics-based modeling works very well and is widely used in many real world applications. However, it can’t always be applied to every situation.
missing information
incomplete awareness of the model state space.
limitations on the available operational data.
For large scale systems, not only are they difficult to model from first principles, it is also not always possible to simulate the system in real time.
Data-driven approaches for systems modeling are an alternative in these situations but can come with their own disadvantages.
Can take a lot of data to train and may behave unpredictably outside the distribution of training data in unobserved regions of the system state space.
In addition, modern neural network approaches don’t typically provide constraints enforcement within physically realizable and operationally safe bounds,

## Slide 30: Asymptotic Stability of Deep Neural Dynamics
  Jan Drgona, Aaron Tuor, Soumya Vasisht, Elliott Skomski, Draguna Vrabie, Spectral Analysis and Stability of Deep Neural Dynamics, arXiv:2011.13492
Notes: The presentation I’m giving today is for a data-driven method for dynamics modeling.
We should care about this because people interact with and depend on complicated systems all the time.
Greater understanding of these systems can lead to outcomes which are
More energy efficient
Cost effective
Conducive to human life
Having an accurate model of a system enables scientific discovery,
Can provide critical information to support high stakes decisions in changing environments
Or to provide necessary information for predictive maintenance of high value equipment, avoiding costly and potentially dangerous equipment
Failures.
One of the most common and lucrative uses of systems models are for predictive control in manufacturing and other large scale enterprises.
I’m presenting a method today which bridges benefits of traditional physics-based modeling with more recent data-driven modeling using deep learning
Traditional physics-based modeling works very well and is widely used in many real world applications. However, it can’t always be applied to every situation.
missing information
incomplete awareness of the model state space.
limitations on the available operational data.
For large scale systems, not only are they difficult to model from first principles, it is also not always possible to simulate the system in real time.
Data-driven approaches for systems modeling are an alternative in these situations but can come with their own disadvantages.
Can take a lot of data to train and may behave unpredictably outside the distribution of training data in unobserved regions of the system state space.
In addition, modern neural network approaches don’t typically provide constraints enforcement within physically realizable and operationally safe bounds,

## Slide 31: Dynamical Effects of Weights
  Jan Drgona, Aaron Tuor, Soumya Vasisht, Elliott Skomski, Draguna Vrabie, Spectral Analysis and Stability of Deep Neural Dynamics, arXiv:2011.13492

## Slide 32: Dynamical Effects of Activation Functions
  Jan Drgona, Aaron Tuor, Soumya Vasisht, Elliott Skomski, Draguna Vrabie, Spectral Analysis and Stability of Deep Neural Dynamics, arXiv:2011.13492

## Slide 33: Attractors of Deep Neural Networks
  Jan Drgona, Aaron Tuor, Soumya Vasisht, Elliott Skomski, Draguna Vrabie, Spectral Analysis and Stability of Deep Neural Dynamics, arXiv:2011.13492

## Slide 34: Attractors of Deep Neural Networks
  Jan Drgona, Aaron Tuor, Soumya Vasisht, Elliott Skomski, Draguna Vrabie, Spectral Analysis and Stability of Deep Neural Dynamics, arXiv:2011.13492

## Slide 35: Conclusion
Differentiable Predictive Control
  Neural state space model for system ID
  Physics-informed priors (neural gray-box)
  Incorporating operational constraints
  Theoretical connection with MPC
  Explicit neural control policies
  Embedded implementation with low-cost HW
  Learning from small datasets
Ongoing work
  Uncertainty Quantification
  Theoretical guarantees: convergence, stability, constraints satisfaction
Software development
  User-friendly software package
    Pytorch-based will be released soon: https://github.com/pnnl/neuromancer
  Suite of structured linear algebra priors
    Structured linear maps in Pytorch: https://pnnl.github.io/slim/
Long-Term Vision
  Causal discovery, dynamical coupling
  Solving large-scale non-convex constrained optimization problems
  Real world applications in energy, manufacturing, cyber

## Slide 36: Dynamical Effects of Network Depth
Unstable layers imply exploding gradient problem
Exponentially stable layers
imply vanishing gradient problem
Network with energy conversion prevents gradient problems
  Jan Drgona, Aaron Tuor, Soumya Vasisht, Elliott Skomski, Draguna Vrabie, Spectral Analysis and Stability of Deep Neural Dynamics, arXiv:2011.13492